| 7 MGD STP SONIA VIHAR Daily Laboratory Analysis Report | Date 15.09.2026 |
| --- | --- |

| Parameter | Permissible Limit | Inlet | Outlet |
| --- | --- | --- | --- |
| Flow MGD | MGD | 0.71 | 0.635 |
| Temperature (°C) | — | 30.2 | 30.4 |
| pH | 5.5 – 9.0 | 7.3 | 7.5 |
| BOD (mg/l) | ≤ 10 | 140 | 4 |
| COD (mg/l) | ≤ 50 | 480 | 44 |
| TSS (mg/l) | ≤ 10 | 268 | 5 |
| Phosphorus (mg/l) | ≤ 1 | 4.2 | 1.3 |
| Total Alkalinity (mg/l) | — | 300 | 230 |
| Dissolved Oxygen – DO (mg/l) | — | NIL | 1.4 |
| Total Nitrogen – TN (mg/l) | ≤ 10 | 40.6 | 8.8 |
| NH4-N (mg/l) | — | 30.8 | 3 |
| Oil & Grease (mg/l) | — | - | - |
| Total Coliform (MPN/100 ml) | ≤ 100 | -- | -- |

■ Shaded outlet value exceeds the permissible discharge limit.

OLMS Photograph 				Inlet & Outlet Sample Photograph

Power Consumption

| Energy Meter | Open | Close | Difference |
| --- | --- | --- | --- |
| Meter - 1 | 154.04 | 154.40 | 0.36 |
| Total Reading | Multiplication Factor | Total Unit (kW) | P.F. |
| 0.36 | 2000 | 720 | 0.98 |